Provide a water level control system including a NEMA4X control panel, solid probes for water level sensing, and a stilling chamber.  The control system shall monitor the water level in the cold water basin to determine level events used to control cold water make-up of the system.  The system shall use a sensor made up of at least two solid stainless steel sensor probes: (1-initiates drain, 1-stops drain).  The control panel shall use electromechanical relays to provide power for the solenoid and electrical contacts for alarms, valves, pumps, and shutdown control circuitry.  The control panel shall use an electromechanical relay to provide power for the solenoid and electrical contacts for alarms, valves, pumps, and shutdown control circuitry: (1-drain relay).  An LED indicator shall light when the switch is activated.  Control panel shall provide dry contacts for the switch for BMS/BAS, fire panel, or other remote monitor.  There shall be a separate fault dry contact for sensor probe foul or power loss.  Requires push-button to test the power relay.

Sensor probes shall be solid stainless steel rods contained in a stilling chamber to minimize turbulence.  Probes will have the ability to add tips as desired, allowing for field adjustable water level height.  Based on Waterline Controls WLC-7000.