Provide a water level control system including a NEMA4X control panel, solid probes for water level sensing, and a stilling chamber.  The control system shall monitor the water level in the cold water basin to determine level events used to control cold water make-up of the system.  The system shall use a sensor made up of at least three solid stainless steel sensor probes: (1-initiates fill 1, 1-initiates fill 2, 1-stops fill 1 & 2).  Initiation of fill 1 and 2 shall alternate.  The control panel shall use two electromechanical relays to provide power for the solenoid and electrical contacts for alarms, valves, pumps, and shutdown control circuitry: (1-fill 1 relay, 1-fill 2 relay).  A separate LED indicator shall light when each switch is activated.  Control panel shall provide separate dry contacts corresponding to each individual switch for BMS/BAS, fire panel, or other remote monitor.  There shall be a separate fault dry contact for sensor probe foul or power loss.  Requires push-button test the power relays.

Sensor probes shall be solid stainless steel rods contained in a stilling chamber to minimize turbulence.  Probes will have the ability to add tips as desired, allowing for field adjustable water level height.  Based on Waterline Controls WLC 4100.