Provide a water level monitoring system including a NEMA4X control panel, solid probes for water level sensing, and a stilling chamber.  The control system shall monitor the water level in the cold water basin to determine level events used to control cold water make-up of the system.  The system shall use a sensor made up of at least six solid stainless steel sensor probes: (1-initiates 0%, 1-indicates 20%, 1-indicates 40%, 1-indicates 60%, 1-indicates 80%, 1-indicates 100%,).  The control panel shall use electrical contacts for control circuitry: (1-0%, 1-20%, 1-40%, 1-60%, 1-80%, 1-100%).  A separate LED indicator shall light when each switch is activated.  Control panel shall provide separate dry contacts corresponding to each individual switch for BMS/BAS, fire panel, or other remote monitor.  There shall be a separate fault dry contact for sensor probe foul or power loss..

Sensor probes shall be solid stainless steel rods contained in a stilling chamber to minimize turbulence.  Probes will have the ability to add tips as desired, allowing for field adjustable water level height.  Based on Waterline Controls WLI Water Level Indicator.